## INV_DARK_DR2_GR
GR |  |  |  |  | MODEL NAMES
[5 empty] | DR2VI-09WFI/ DR2VO-09 | DR2VI-12WFI/ DR2VO-12 | DR2VI32-18WFI/ DR2VO32-18 | DR2VI32-24WFI/ DR2VO32-24
SPECIFICATIONS |  | Ψυκτική Απόδοση (Btu/h) |  |  | 9.000 (2.730-12.620) | 12.000 (3.410-13.650) | 18.000 (4.430-19.790) | 24.000 (7.500-29.000)
|  | Ψυκτική Απόδοση (kWatt) |  |  | 2.6 (0.8-3.2) | 3.5 (1.0-4.0) | 5.0 (1.30-5.80) | 7.0 (2.2-8.5)
|  | Θερμική Απόδοση (Btu/h) |  |  | 11.000 (2.730-14.330) | 14.500 (3.410-17.740) | 18.150 (4.770-20.470) | 28.000 (8.190-34.120)
|  | Θερμική Απόδοση (kWatt) |  |  | 3.2 (0.8-4.2) | 4.2 (1.0-5.2) | 5.2 (1.4-6.0) | 8.1 (2.40-10.0)
|  | Εποχιακή Απόδοση (Σύμφωνα με ΕΝ14825) | Ψύξη | Φορτίο Σχεδιασμού (kW) | 2.6 | 3.5 | 5.0 | 7.0
|  |  |  | Eνεργειακή Κλάση | A+++ | A+++ | A++ | A++
|  |  |  | SEER | 8.5 | 8.5 | 6.1 | 7.1
|  |  |  | Ετήσια Κατανάλωση Ρεύματος (kWh/έτos) | 107 | 144 | 287 | 350
|  |  | Θέρμανση (Μέση Ζώνη) | Φορτίο Σχεδιασμού (kW) | 2.4 | 2.8 | 4.6 | 5.6
|  |  |  | Eνεργειακή Κλάση | A++ | A++ | A+ | A+
|  |  |  | SCOP | 4.6 | 4.6 | 4.0 | 4.0
|  |  |  | Ετήσια Κατανάλωση Ρεύματος (kWh/έτos) | 731 | 854 | 1610 | 1963
|  |  | Θέρμανση (Θερμή Ζώνη) | Φορτίο Σχεδιασμού (kW) | 2.3 | 2.8 | 4.6 | 5.6
|  |  |  | Eνεργειακή Κλάση | A+++ | A+++ | A+++ | A+++
|  |  |  | SCOP | 5.1 | 5.1 | 5.1 | 5.1
|  |  |  | Ετήσια Κατανάλωση Ρεύματος (kWh/έτos) | 6.31 | 768 | 1263 | 1537
|  | Τάση/ Συχνότητα/Φάση (V/Hz/Ph) |  |  | 230/50/1 | 230/50/1 | 230/50/1 | 230/50/1
|  | Ρεύμα Λειτουργίας (Α) |  | Ψύξη | 2.9 (0.9-6.7) | 3.9 (1.4-6.7) | 6.5 (1.8-8.9) | 9.6 (3.2-13)
|  |  |  | Θέρμανση | 3.6 (1.3-7.2) | 5.0 (1.3-7.2) | 6.3 (2.3-11.3) | 9.7 (3.2-13)
|  | Κατανάλωση (kW) |  | Ψύξη | 0.65 (0.2-1.5) | 0.87 (0.3-1.5) | 1.46 (0.4-2.0) | 2.16 (0.7-2.9)
|  |  |  | Θέρμανση | 0.8 (0.3-1.6) | 1.1 (0.5-1.6) | 1.4 (0.5-2.5) | 2.18 (0.7-2.9)
|  | Παροχή Αέρα (Turbo/Υψηλή/Μέση/Χαμηλή) (m3/h) |  |  | 650/600/500/450 | 700/650/550/500 | 1.000/900/800/600 | 1.300/1.200/1.000/850
|  | Στάθμη Θορύβου [dB(A)] |  | Εσωτερική Μονάδα (Αθόρυβη/Χαμηλή/Μέση/Υψηλή) | 20/25/30/35 | 22/29/33/38 | 30/35/40/44 | 30/37/43/47
|  |  |  | Εξωτερική Μονάδα | 47 | 48 | 53 | 52
|  | Ηχητική Ισχύς [dB(A)] |  | Εσωτερική Μονάδα | 54 | 56 | 59 | 60
|  |  |  | Εξωτερική Μονάδα | 59 | 61 | 65 | 65
|  | Ικανότητα Αφύγρανσης |  | L/h | 1.2 | 1.6 | 2.0 | 2.8
|  |  |  | L/day | 28.8 | 38.4 | 48.0 | 67.2
|  | Τύπος Συμπιεστή |  |  | ROTARY | ROTARY | ROTARY | ROTARY
|  | Γραμμή Υγρού ¦ Γραμμή Αερίου |  |  | 1/4" ¦ 3/8" | 1/4" ¦ 3/8" | 1/4" ¦ 1/2" | 1/4" ¦ 1/2"
|  | Aσφάλειες Τήξηs (A) |  |  | 10 | 10 | 16 | 16
|  | Καλώδια Εντολών (Noxmm²) |  |  | 4x1.5 | 4x1.5 | 4x1.5 | 4x1.5
|  | Διαστάσεις (MxBxY) (mm) |  | Εσωτερική Μονάδα | 887x211x281 | 887x211x281 | 1.030x233x322 | 1.115x248x336
|  |  |  | Εξωτερική Μονάδα | 800x280x550 | 800x280x550 | 800x280x550 | 890x353x697
|  | Καθαρό Βάρος (kg) |  | Εσωτερική/Εξωτερική | 10.0/29.0 | 10.0/31.5 | 13.0/32.7 | 16.0/47.3
|  | Ψυκτικό Υγρό/Ποσότητα (g) |  |  | R32/650 | R32/940 | R32/900 | R32/1.200
|  | Εύρος Λειτουργίας Εξωτ. Θερμοκρασίας (ºC) |  | Ψύξη | -20~43 | -20~43 | -20~43 | -20~43
|  |  |  | Θέρμανση | -20~24 | -20~24 | -20~24 | -20~24
FEATURES | MAIN USP | Ιονιστής
| 2nd USP | Καινοτόμος Σχεδιασμός
| 3rd USP | Ενεργειακή Κλάση Α+++
| 4th USP | Ροή Αέρα 4ων Κατευθύνσεων
| 5th USP | Wi-Fi Standard - Inventor Control
| other features | Remote on/off
Κεντρικός Έλεγχος
Δυνατότητα Σύνδεσης με BMS
Απόλυτα Αθόρυβη Λειτουργία
Λειτουργία Ψύξης σε Χαμηλές Θερμοκρασίες (-20)
Λειτουργία Θέρμανσης σε Χαμηλές Θερμοκρασίες (-20)
Φίλτρο Σκόνης Αέρα Υψηλής Πυκνότητας
Χρονοδιακόπτης 24 ωρών
Λειτουργία Ύπνου
Αυτόματη Κίνηση Περσίδων
Αποθήκευση Θέσης Περσίδας
Λειτουργία Έξυπνης Προθέρμανσης
Λειτουργία Turbo
Αυτόματη Επανεκκίνηση
Αυτοδιάγνωση Βλαβών
Ανίχνευση Διαρροής Ψυκτικού Μέσου
Δύο Έξοδοι Σύνδεσης Αποστράγγισης
All DC Inverter
R32 Ψυκτικό Μέσο

## INV_DARK_DR2_EN
EN |  |  |  |  | MODEL NAMES
[5 empty] | DR2VI-09WFI/ DR2VO-09 | DR2VI-12WFI/ DR2VO-12 | DR2VI32-18WFI/ DR2VO32-18 | DR2VI32-24WFI/ DR2VO32-24
SPECIFICATIONS |  | Cooling Capacity (Btu/h) |  |  | 9.000 (2.730-12.620) | 12.000 (3.410-13.650) | 18.000 (4.430-19.790) | 24.000 (7.500-29.000)
|  | Cooling Capacity (kWatt) |  |  | 2.6 (0.8-3.2) | 3.5 (1.0-4.0) | 5.0 (1.30-5.80) | 7.0 (2.2-8.5)
|  | Heating Capacity (Btu/h) |  |  | 11.000 (2.730-14.330) | 14.500 (3.410-17.740) | 18.150 (4.770-20.470) | 28.000 (8.190-34.120)
|  | Heating Capacity (kWatt) |  |  | 3.2 (0.8-4.2) | 4.2 (1.0-5.2) | 5.2 (1.4-6.0) | 8.1 (2.40-10.0)
|  | Seasonal Efficiency (In accordance to EN14825) | Cooling | Pdesign (kW) | 2.6 | 3.5 | 5.0 | 7.0
|  |  |  | Energy Class | A+++ | A+++ | A++ | A++
|  |  |  | SEER | 8.5 | 8.5 | 6.1 | 7.1
|  |  |  | Annual Power Consumption (kWh/year) | 107 | 144 | 287 | 350
|  |  | Heating (Middle Zone) | Pdesign (kW) | 2.4 | 2.8 | 4.6 | 5.6
|  |  |  | Energy Class | A++ | A++ | A+ | A+
|  |  |  | SCOP | 4.6 | 4.6 | 4.0 | 4.0
|  |  |  | Annual Power Consumption (kWh/year) | 731 | 854 | 1610 | 1963
|  |  | Heating (Warm Zone) | Pdesign (kW) | 2.3 | 2.8 | 4.6 | 5.6
|  |  |  | Energy Class | A+++ | A+++ | A+++ | A+++
|  |  |  | SCOP | 5.1 | 5.1 | 5.1 | 5.1
|  |  |  | Annual Power Consumption (kWh/year) | 6.31 | 768 | 1263 | 1537
|  | Voltage/Frequency/Phase (V/Hz/Ph) |  |  | 230/50/1 | 230/50/1 | 230/50/1 | 230/50/1
|  | Current Input (A) |  | Cooling | 2.9 (0.9-6.7) | 3.9 (1.4-6.7) | 6.5 (1.8-8.9) | 9.6 (3.2-13)
|  |  |  | Heating | 3.6 (1.3-7.2) | 5.0 (1.3-7.2) | 6.3 (2.3-11.3) | 9.7 (3.2-13)
|  | Power Input (W) |  | Cooling | 0.65 (0.2-1.5) | 0.87 (0.3-1.5) | 1.46 (0.4-2.0) | 2.16 (0.7-2.9)
|  |  |  | Heating | 0.8 (0.3-1.6) | 1.1 (0.5-1.6) | 1.4 (0.5-2.5) | 2.18 (0.7-2.9)
|  | Air Flow Volume (Turbo/High/Medium/Low) (m3/h) |  |  | 650/600/500/450 | 700/650/550/500 | 1.000/900/800/600 | 1.300/1.200/1.000/850
|  | Noise Level [dB(A)] |  | Indoor unit (Silent/Low/Medium/High) | 20/25/30/35 | 22/29/33/38 | 30/35/40/44 | 30/37/43/47
|  |  |  | Outdoor unit | 47 | 48 | 53 | 52
|  | Sound Power Level [dB(A)] |  | Indoor unit | 54 | 56 | 59 | 60
|  |  |  | Outdoor unit | 59 | 61 | 65 | 65
|  | Dehumidifying Volume |  | L/h | 1.2 | 1.6 | 2.0 | 2.8
|  |  |  | L/day | 28.8 | 38.4 | 48.0 | 67.2
|  | Compressor Type |  |  | ROTARY | ROTARY | ROTARY | ROTARY
|  | Liquid line ¦ Gas line |  |  | 1/4" ¦ 3/8" | 1/4" ¦ 3/8" | 1/4" ¦ 1/2" | 1/4" ¦ 1/2"
|  | Fuses (A) |  |  | 10 | 10 | 16 | 16
|  | Signal Wires (Noxmm²) |  |  | 4x1.5 | 4x1.5 | 4x1.5 | 4x1.5
|  | Dimensions (WxDxH) (mm) |  | Indoor unit | 887x211x281 | 887x211x281 | 1.030x233x322 | 1.115x248x336
|  |  |  | Outdoor unit | 800x280x550 | 800x280x550 | 800x280x550 | 890x353x697
|  | Net Weight (kg) |  | Indoor/Outdoor | 10.0/29.0 | 10.0/31.5 | 13.0/32.7 | 16.0/47.3
|  | Refrigerant/Charge (g) |  |  | R32/650 | R32/940 | R32/900 | R32/1.200
|  | Outdoor Operation Temperature Range (ºC) |  | Cooling | -20~43 | -20~43 | -20~43 | -20~43
|  |  |  | Heating | -20~24 | -20~24 | -20~24 | -20~24
FEATURES | MAIN USP | Ionizer
| 2nd USP | Innovative Design
| 3rd USP | A+++ Energy Class
| 4th USP | 4 Way Air Flow
| 5th USP | Wi-Fi Standard - Inventor Control
| other features | Remote on/off
Central Control
Connectivity with BMS
Ultra Silence Mode
Low Ambient Cooling at -20°C
Low Ambient Heating at -20°C
High Density Air Dust Filter
24-hour Timer
Sleep Mode
Auto Swing Louver
Louver Angle Memory
Hot Start
Turbo Mode
Auto Restart
Auto Error Diagnosis
Refrigerant Leakage Detect
Two-way Draining
All DC Inverter
R32 ECO Refrigerant

## INV_DARK_DR2_RO
RO |  |  |  |  | MODEL NAMES
[5 empty] | DR2VI-09WFI/ DR2VO-09 | DR2VI-12WFI/ DR2VO-12 | DR2VI32-18WFI/ DR2VO32-18 | DR2VI32-24WFI/ DR2VO32-24
SPECIFICATIONS |  | Capacitate Răcire (Btu/h) |  |  | 9.000 (2.730-12.620) | 12.000 (3.410-13.650) | 18.000 (4.430-19.790) | 24.000 (7.500-29.000)
|  | Capacitate Răcire (kWatt) |  |  | 2.6 (0.8-3.2) | 3.5 (1.0-4.0) | 5.0 (1.30-5.80) | 7.0 (2.2-8.5)
|  | Capacitate Încălzire (Btu/h) |  |  | 11.000 (2.730-14.330) | 14.500 (3.410-17.740) | 18.150 (4.770-20.470) | 28.000 (8.190-34.120)
|  | Capacitate Încălzire (kWatt) |  |  | 3.2 (0.8-4.2) | 4.2 (1.0-5.2) | 5.2 (1.4-6.0) | 8.1 (2.40-10.0)
|  | Eficiență Sezonieră (în conformitate cu EN14825) | Răcire | Pdesign (kW) | 2.6 | 3.5 | 5.0 | 7.0
|  |  |  | Clasă Energetică | A+++ | A+++ | A++ | A++
|  |  |  | SEER | 8.5 | 8.5 | 6.1 | 7.1
|  |  |  | Consum energetic anual (kW/an) | 107 | 144 | 287 | 350
|  |  | Încălzire (Zona Medie) | Pdesign (kW) | 2.4 | 2.8 | 4.6 | 5.6
|  |  |  | Clasă Energetică | A++ | A++ | A+ | A+
|  |  |  | SCOP | 4.6 | 4.6 | 4.0 | 4.0
|  |  |  | Consum energetic anual (kW/an) | 731 | 854 | 1610 | 1963
|  |  | Încălzire (Zona Caldă) | Pdesign (kW) | 2.3 | 2.8 | 4.6 | 5.6
|  |  |  | Clasă Energetică | A+++ | A+++ | A+++ | A+++
|  |  |  | SCOP | 5.1 | 5.1 | 5.1 | 5.1
|  |  |  | Consum energetic anual (kW/an) | 6.31 | 768 | 1263 | 1537
|  | Voltaj/Frecvență/Fază (V/Hz/Ph) |  |  | 230/50/1 | 230/50/1 | 230/50/1 | 230/50/1
|  | Intensitate curent (A) |  | Răcire | 2.9 (0.9-6.7) | 3.9 (1.4-6.7) | 6.5 (1.8-8.9) | 9.6 (3.2-13)
|  |  |  | Încălzire | 3.6 (1.3-7.2) | 5.0 (1.3-7.2) | 6.3 (2.3-11.3) | 9.7 (3.2-13)
|  | Consum energetic (W) |  | Răcire | 0.65 (0.2-1.5) | 0.87 (0.3-1.5) | 1.46 (0.4-2.0) | 2.16 (0.7-2.9)
|  |  |  | Încălzire | 0.8 (0.3-1.6) | 1.1 (0.5-1.6) | 1.4 (0.5-2.5) | 2.18 (0.7-2.9)
|  | Debit de aer (Turbo/Mare/Medie/Mică) (m3/h) |  |  | 650/600/500/450 | 700/650/550/500 | 1.000/900/800/600 | 1.300/1.200/1.000/850
|  | Nivel de zgomot [dB(A)] |  | Unitate Interioară (Mut/Mi/Me/Ma) | 20/25/30/35 | 22/29/33/38 | 30/35/40/44 | 30/37/43/47
|  |  |  | Unitate exterioară | 47 | 48 | 53 | 52
|  | Nivel sunet [dB(A)] |  | Unitate Interioară | 54 | 56 | 59 | 60
|  |  |  | Unitate exterioară | 59 | 61 | 65 | 65
|  | Volum dezumidificare |  | L/h | 1.2 | 1.6 | 2.0 | 2.8
|  |  |  | L/day | 28.8 | 38.4 | 48.0 | 67.2
|  | Tip compresor |  |  | ROTARY | ROTARY | ROTARY | ROTARY
|  | Traseu lichid / Traseu gaz |  |  | 1/4" ¦ 3/8" | 1/4" ¦ 3/8" | 1/4" ¦ 1/2" | 1/4" ¦ 1/2"
|  | Siguranțe (A) |  |  | 10 | 10 | 16 | 16
|  | Cablu comunicare (Noxmm²) |  |  | 4x1.5 | 4x1.5 | 4x1.5 | 4x1.5
|  | Dimensiuni (LxAxÎ) (mm) |  | Unitate interioară | 887x211x281 | 887x211x281 | 1.030x233x322 | 1.115x248x336
|  |  |  | Unitate exterioară | 800x280x550 | 800x280x550 | 800x280x550 | 890x353x697
|  | Greutate netă (kg) |  | Interioară/Exterioară | 10.0/29.0 | 10.0/31.5 | 13.0/32.7 | 16.0/47.3
|  | Agent frigorific/Incarcare (g) |  |  | R32/650 | R32/940 | R32/900 | R32/1.200
|  | Interval temperaturi funcționare (ºC) |  | Răcire | -20~43 | -20~43 | -20~43 | -20~43
|  |  |  | Încălzire | -20~24 | -20~24 | -20~24 | -20~24
FEATURES | MAIN USP | Aqua Ionizator
| 2nd USP | Concept inovator
| 3rd USP | Clasa Energetica A+++
| 4th USP | Flux de Aer in 4 Directii
| 5th USP | Wi-Fi Standard
| other features | Remote On/Off
Control centralizat
Conectivitate cu BMS
Modul Ultra Silentios
Racire la temperaturi scazute -20Cº
Racire la temperaturi scazute de -20°C
Filtru de praf de mare densitate
Programator 24 Ore
Functia Sleep Mode
Miscare Automata a Flapsurilor
Functia de Memorare a Pozitiei Flapsurilor
Functia Hot Start
Mod Turbo
Auto Restart
Autodiagnosticare a Erorilor
Detectare Scurgere Freon
2 Cai de Scurgere a Condensului
All DC Inverter
R32 ECO Freon